## Calculator
Instructions for using this calculator: It is important to read and follow these instructions carefully!
Note: A PASS indicates volts drop is within acceptible range only. Good wiring practice and guidance within installation instructions must still be followed.
Enter required values described below into pale yellow boxes within user section:
1: | Input the total modules (ZCM's or Relays) on the longest single circuit only. Ignore any tee offs .
2: | Use the drop down menu to select Conductor size = This is the CSA of cable to be used to wire the system. Available common cable sizes are:
|  | 0.5mm | (Usually 'Beldon' or comms Cabe, Not Recomended)
|  | 0.75mm | (this is 'standard' flex)
1.0mm
1.5mm
2.0mm
2.5mm
|  | 4.0mm | (this size and above could be singles, but is generally only in SWA)
Note on cable size: Any cable size above 1.5mm when paired will not fit directly into the ZCM. We strongly recommend using ferrules.
For the same conductor size only use a. If you have used different cable sizes (i.e. Larger sized 'backbone' up riser, then tee off on individual floors with smaller cable) they must be input as described below:
2a: This must be the first leg or 'backbone' of the system (i.e. connected to the panel).
2b: This must be the second part of the circuit (i.e a tee off or extension).
3: | Length of circuit = This is the whole run length of the longest part of any single circuit, from generator to last ZCM. Ignoring any tee offs. If the circuit branches, only consider the longest branch.
For the same length of circuit only use a. If you have used different cable sizes for the runs (i.e. Larger sized 'backbone' up riser, then tee off on individual floors with smaller cable) they must be input as described below:
3a: This must be the first leg or 'backbone' of the system (i.e. connected to the panel).
3b: This must be the second part of the circuit (i.e a tee off or extension).
4: | Distrubution of zone control modules (ZCM) along circuit. Three options available. (if second cable size used it assumed that modules will be mainly on this length so END should always be selected)
EVEN: Modules are distributed at regular intervals along the circuit length.
END: Module distribution is biased towards the end of the circuit (i.e. top floor of a hotel).
UNKNOWN: If you are unsure for safety the calculator will assume a 'worst case scenario'
5: | A fail indicates the circuit may need re-designing. Possible fixes include:
Using larger csa cable for one or, if applicable, both parts of the circuit
Redesigning cable routes decreasing circuit length
Redesigning system for more circuits of shorter lengths
Redeploying ZCM's more evenly throughout the system
6: | Indicates if additional fieldbus generators required. A maximum of 100 devices (ZCM's or relays) can be fitted to any fieldbus generator. Up to seven generators can be fitted to a single gateway
User Section: enter values into boxes
|  | 1 |  | Total modules on the circuit: | 4 | ZCM
|  | 2 |  | Conductor Size a: | 1 | mm²
|  |  |  | Conductor Size b: |  | mm²
|  | 3 |  | Length of Circuit a: | 200 | Metres
|  |  |  | Length of Circuit b: |  | Metres
|  | 4 |  | Distribution of Modules: | END
|  | 5 | 7.87
7.87
|  | 6 | 4
CHECK SYSTEM
CLICK HERE FOR EXAMPLE DIAGRAMS

## Example Diagrams
BACK TO CALCULATOR

## Foglio1 (hidden)
Voltage Drop Calculation | Value a | Value b | NOTES
Conductor sections[mm2] | 1 | 1 | EXAMPLE CALCULATION | [5 empty] | 0.5
Conductor length [m] | 200 | 0 | Consumption of 25 BDA RE13A-U = 25mA | [5 empty] | 0.75
I BUS DC [mA] | 8 |  | Consumption of 14 SHSUT = 28 mA | [5 empty] | 1
|  |  | I BUS= 25+28 = 53 mA | [5 empty] | 1.5
2
R single conductor [Ohm] | 3.9 | 0 | R(single cable) = 0,0195 *length[m]/Section[mm2] | [5 empty] | 2.5
4
∆V [V](load at the end of the network) | 0.1248 | 0.1248 | ∆V [V] = 2*R*I*2
Vbus [V] (load at the end of the network) | 7.8752 | 0 | V BUS [V]= 8 - ∆V
Coefficient for the load distribution | 0.65 | 0.65
∆V [V] (load distributed evenly) | 0.08112 | 0.08112 | 2*R = D+ and D- (two cables)
Vbus [V] (load distributed evenly) | 7.9189 | 0 | I*2 = we double the current to calculate the worst case: all output channels activated at the same time (duty cycle of 0,5)
VBUS must be 5,5 V or higher
7.8752
| 7.87 |  | If the load is distributed evenly you have to multiply the ∆V by a constant value of 0,65
7.87
Result | 7.87 |  | In this example: 1000 m (load distributed evenly) ----> ∆V=1.07 V, VBUS=6.93 and the section of the cable is 2,5mm2
8
a = conductor size |  | User Section: enter values into boxes |  |  |  |  | END | END
b = length of run |  |  |  | Conductor Size a: | 1 | mm² | EVEN
c = ZCM x 2 on circuit being calculated |  |  |  | Conductor Size b: | 1 | mm² | UNKNOWN
d = Green is ok Red will not work |  |  |  | Length of Circuit a: | 200 | Metres
|  |  |  | Length of Circuit b: | 0 | Metres
|  |  |  | Distribution: | END
|  |  |  | Total modules on the circuit: | 4 | ZCM
PASS - Circuit Design is Good
FAIL - Circuit Outside Acceptable Parameters